## Purpose and Background
NERC LIST OF ACCEPTABLE MODELS FOR INTERCONNECTION-WIDE MODELING
Purpose
The purpose of this list of acceptable models is to develop and maintain a repository of models deemed acceptable by the ERO and industry stakeholders for use in developing interconnection-wide models developed by the MOD-032 Designee. The NERC System Analysis and Modeling Subcommittee (SAMS) initially developed this list and is maintained and updated by NERC Advanced Systems Analytics and Modeling.
This list seeks to bring together multiple sources of data to ensure uniformity in the use of models across interconnections. While models may be deemed 'obsolete' or 'deprecated' due to known issues, those models are not removed from the software vendor libraries for various reasons. However, those models should not be used for developing interconnection-wide models.
Table Legend
Yellow: Use of this model is not recommended. Other models may be more appropriate for use. While existing models in the cases may still use these models, their future use is discouraged. Resubmission of models as per MOD-026-1 and MOD-027-1 for existing resources should convert the existing model to a more representative model.
Orange: Use of this model for new resources or resources re-certifying their models as per MOD-026-1 and MOD-027-1 should be prohibited, unless specifically acceptable by the Modeling Designee for interconnection-wide base case creation. Known modeling issues, errors, or deficiencies exist with this model. Modeling Designees should consider proactive actions to move towards more representative and accurate models.
Blue: These models are industry-accepted (e.g., IEEE standard models) that have not yet been implemented by the software vendors. Therefore they are listed on the list of acceptable models for tracking purposes using this color and will be updated accordingly once implemented by the software vendors. This is intended to provide direction to software vendors on which models industry recommends being implemented with higher priority.
Disclaimers and Notes
> Some of the models in this list may not be acceptable for use by all Modeling Designees. Modeling requirements as specified for each interconnection by the Modeling Designees supercede this list and those Designees should be consulted directly.
> 'Black box' models (e.g., no block diagrams, no source code, no documentation) are prohibited for use in interconnection-wide models.
> This list of models may not be comprehensive of all models available in the various commercial software platforms. Additional models may exist in the software platforms and are not addressed in this list of acceptable models. Models not listed on this list of acceptable models (e.g., available in later versions of the software, or manufacturer-specific models) are considered acceptable assuming they are not "black box" models.
> User-defined models are not acceptable unless either 1) the Modeling Designee allows them, or 2) a currently available generic model cannot be demonstrated with documentation to adequately represent the resource (e.g., wind power plants). Some exceptions to this exist such as HVDC circuits. > In PSS®E, the "U1" versions of models are not considered user-defined models. > Standard library models are not considered user-defined models.
Questions
Please direct any questions to NERC Advanced System Analytics and Modeling (AdvancedSystemAnalyticsModeling@nerc.net).

## NERC Acceptable Models List
NERC LIST OF ACCEPTABLE MODELS FOR INTERCONNECTION-WIDE MODELING
Use of this model is not recommended. Other models are more suitable.
Use of this model is considered unacceptable. Future model submittals or renewals using this model should be prohibited. Modeling limitations or discrepancies known.
Tracking of industry-accepted models that are not yet been implemented by the software vendors.
Model Type | Model Description | Unacceptable Models | Siemens PSSE | GE PSLF | PowerWorld Simulator |  | PowerTech DSATools |  | V&R Energy POM |  | Comments | Reference
[5 empty] | PSSE | PSLF | PSSE | PSLF | PSSE | PSLF
Machine Model | Round Rotor Generator Model (IEEE Std 1110 §5.3.2 Model 2.2) |  | GENROU | genrou | X | X | X | X | X | X | Treatment of saturation. Use GENTPJ. See Modeling Notification. | Modeling Notification - Use of GENTPJ
| Salient Pole Generator Model (IEEE Std 1110 §5.3.1 Model 2.1) | ü | GENSAL | gensal | X | X | X | X | X | X | Treatment of saturation. Use GENTPJ. See Modeling Notification. | Modeling Notification - Use of GENTPJ
| Round Rotor Generator Model (IEEE Std 1110 §5.3.2 Model 2.2) |  | GENROE | -- | X | -- | X | -- | X | -- | Treatment of saturation. Use GENTPJ. See Modeling Notification. | Modeling Notification - Use of GENTPJ
| Salient Pole Generator Model (IEEE Std 1110 §5.3.1 Model 2.1) |  | GENSAE | -- | X | -- | X | -- | X | -- | Treatment of saturation. Use GENTPJ. See Modeling Notification. | Modeling Notification - Use of GENTPJ
| Round Rotor Generator with DC Offset Torque Component |  | GENDCO | gensdo | X | -- | -- | -- | -- | --
| Cross Compound WECC Type F |  | -- | gencc | -- | X | -- | X | -- | X
| Generator Type F |  | -- | gentpf | -- | X | -- | X | -- | X
| Generator Type J |  | GENTPJ1 | gentpj | -- | X | X | X | -- | X
| Classical Generator Model (IEEE Std 1110 §5.4.2) | ü | GENCLS | gencls | X | X | X | X | X | X | Does not allow for representation of excitation system and turbine/speed governor models. | SME input.
| Third Order Generator Model |  | CGEN1 | -- | -- | -- | X | -- | -- | -- | Specialized model (Ontario-Hydro model (and IEEE Std. 1110)) that goes to sub-sub-transient effects (up to 3 windings in the d- or q-axis) for special cases.
| Transient Level Generator Model | ü | GENTRA | -- | X | -- | X | -- | -- | -- | Simplified model without subtransient effects; prone to numerical problems. | PSS/E PAG V2, Section 14.4.5.4
| Salient Pole Frequency Changer Model |  | FRECHG | -- | -- | -- | -- | -- | -- | --
| Synchronous Generator Model combining GENQSC and GENESC |  | -- | genqec | -- | -- | -- | -- | -- | -- |  | See references [16] and [17] at bottom of Excel sheet
| "Two-cage" or "One-Cage" Induction Generator |  | CIMTR1, CIMTR3 | genind | X | X | -- | -- | -- | --
Signal Playback Models | Play-In of Voltage and/or Frequency Signal |  | PLBVF1 | gencls | X | -- | X | X | -- | --
| Frequency Playback Model |  | PLBVF1 | gencls | X | -- | X | X | -- | --
| Play-In of Generator Field Voltage |  | -- | plefd | X | -- | X | X | -- | --
| Delivers Played-In Signal to Dynamic Simulation Models |  | -- | plnow | -- | -- | X | X | -- | --
| Play-In of Voltage Regulator and Governor Reference Settings |  | -- | plref | X | -- | X | X | -- | --
| Play-In Turbine Power |  | -- | pltp | X | -- | X | X | -- | --
| Thevenin Source of Defined Voltage Amplitude and Frequency |  | -- | gthev | -- | -- | X | X | -- | --
Renewable Energy Resource Models | Generic Type 1 WTG Generator Model (Fixed-speed induction generator) |  | WT1G1 | wt1g | X | X | X | X | X | X
| Generic Type 2 WTG Generator Model (Variable slip induction generator with variable rotor resistance) |  | WT2G1 | wt2g | X | X | X | X | X | X
| Generic Type 3 WTG Generator/Converter Model - PSSE (Doubly-fed induction generator) | ü | WT3G1 | -- | X | -- | X | -- | X | -- | 2nd Generation Renewable Models replace these; numerical issues in base cases. | WECC Wind Modeling Guideline
| Generic Type 3 WTG Generator/Converter Model - PSLF (Doubly-fed induction generator) | ü | WT3G2 | wt3g | X | X | X | X | X | X | 2nd Generation Renewable Models replace these; numerical issues in base cases. | WECC Wind Modeling Guideline
| Generic Type 4 WTG Generator/Converter Model - PSSE (Variable speed generator with full converter) | ü | WT4G1 | -- | X | -- | X | -- | X | -- | 2nd Generation Renewable Models replace these; numerical issues in base cases. | WECC Wind Modeling Guideline
| Generic Type 4 WTG Generator/Converter Model - PSLF (Variable speed generator with full converter) | ü | WT4G2 | wt4g | -- | X | -- | X | X | X | 2nd Generation Renewable Models replace these; numerical issues in base cases. | WECC Wind Modeling Guideline
| Generic Type 2 WTG Rotor Resistance Control Model |  | WT2E1 | wt2e | X | X | X | X | X | X
| Generic Type 3 WTG Electrical Control Model | ü | WT3E1 | wt3e | X | X | X | X | X | X | 2nd Generation Renewable Models replace these; numerical issues in base cases. | WECC Wind Modeling Guideline
| Generic Type 4 WTG Electrical Control Model - PSSE | ü | WT4E1 | -- | X | -- | X | -- | X | -- | 2nd Generation Renewable Models replace these; numerical issues in base cases. | WECC Wind Modeling Guideline
| Generic Type 4 WTG Electrical Control Model - PSLF | ü | WT4E2 | wt4e | -- | X | -- | X | X | X | 2nd Generation Renewable Models replace these; numerical issues in base cases.
| Generic Type 1 Two Mass Turbine Model |  | WT12T1 | wt1t | X | X | X | X | X | X
| Generic Type 2 Two Mass Turbine Model |  | WT12T1 | wt2t | X | X | X | X | X | X
| Generic Type 3 WTG Turbine Model | ü | WT3T1 | wt3t | X | X | X | X | X | X | 2nd Generation Renewable Models replace these; numerical issues in base cases. | WECC Wind Modeling Guideline
| Generic Type 3 and 4 WTG Drive Train Model |  | WTDTA1 | wtgt_a | X | X | X | X | X | X
| Generic Type 3 and 4 WTG Drive Train Model |  | -- | wtgt_b | -- | -- | -- | -- | -- | --
| Generic Type 3 WTG Pitch Control Model | ü | WT3P1 | wt3p | X | X | X | X | X | X | 2nd Generation Renewable Models replace these; numerical issues in base cases. | WECC Wind Modeling Guideline
| Generic Type 3 and 4 WTG Pitch Control Model |  | WTPTA1 | wtgp_a | X | X | X | X | X | X
| Generic Type 3 and 4 WTG Pitch Control Model |  | -- | wtgp_b | -- | -- | -- | -- | -- | --
| Generic Type 1 and 2 WTG Pitch Control Model | ü | WT12A1 | wt1p, wt2p | X | X | X | X | X | X | Does not accurately represent Type 1 WTG pitch controls. | SME input.
| Generic Type 2 and 2 WTG Pitch Control Model |  | WT12A1U_B | wt1p_b | -- | X | -- | -- | -- | --
| Generic Type 3 and 4 WTG Aerodynamics Model |  | WTARA1 | wtga_a | X | X | X | X | X | X
| Generic Type 3 and 4 WTG Torque Control Model |  | WTTQA1 | wtgq_a | X | X | X | X | X | X
| Generic Type 4 WTG Power Converter Model | ü | -- | wt4t | -- | X | -- | X | -- | X | 2nd Generation Renewable Models replace these; numerical issues in base cases. | WECC Wind Modeling Guideline
| Generic Type 4 Pitch Control Model | ü | -- | wt4p | -- | -- | -- | X | -- | X | 2nd Generation Renewable Models replace these; numerical issues in base cases. | WECC Wind Modeling Guideline
| Linearized Model of PV Panel Output Curve |  | PANELU1 | -- | -- | -- | -- | -- | -- | --
| Linearized Model of PV Panel Solar Irradiance Profile |  | IRRADU1 | -- | -- | -- | -- | -- | -- | --
| Generic Phase 2 Renewable Energy Generator/Converter Model |  | REGCA1 | regc_a | X | X | X | X | -- | --
| Generic Phase 2 Renewable Energy Generator/Converter Model |  | -- | regc_b | -- | -- | -- | -- | -- | --
| Generic Phase 2 Renewable Energy Electrical Controls Model |  | REECA1 | reec_a | X | X | X | X | X | X
| Generic Phase 2 Renewable Energy Plant Controller |  | REPCA1 | repc_a | X | X | X | X | X | X
| Generic Plant Control Model |  | PLNTBU1 | repc_b | -- | -- | -- | -- | -- | -- | This should be used in coordination with the auxiliary control models "AXBU1"; otherwise, use REPCA.
| Generic Phase 2 PV Electrical Controls Model |  | REECB1 | reec_b | X | X | X | X | X | X | Use REEC_A to represent equipment. This model lacks the VDL logic, namely momentary cessation | Modeling Notification
| Generic Phase 2 Energy Storage Electrical Controls |  | REECCU1/REECC1 | reec_c | -- | X | -- | X | -- | --
| Generic Phase 2 Renewable Energy Electrical Controls Model |  | -- | reec_d | -- | -- | -- | -- | -- | --
| Generic Phase 2 Renewable Energy Auxiliary Control Model - Type 3 WTGs |  | REAX3BU1 | -- | -- | -- | -- | -- | -- | --
| Generic Phase 2 Renewable Energy Auxiliary Control Model - Type 4 WTGs and Solar PV |  | REAX4BU1 | -- | -- | -- | -- | -- | -- | --
| Generic Phase 2 Renewable Energy Auxiliary Control Model - SVC |  | SVCAXBU1 | -- | -- | -- | -- | -- | -- | --
| Generic Phase 2 Renewable Energy Auxiliary Control Model - FACTS Device |  | FCTAXBU1 | -- | -- | -- | -- | -- | -- | --
| Generic Phase 2 Renewable Energy Auxiliary Control Model - Synchronous Condenser |  | SYNAXBU1 | -- | -- | -- | -- | -- | -- | --
| Vestas Model of Wound-Rotor Induction Generator (with Variable External Rotor Resistance) |  | -- | genwri | -- | X | -- | X | -- | X | 2nd Generation Renewable Models should replace these; potential numerical issues in base cases.
| Vestas Model of Rotor Resistance Control for Wound-Rotor Induction WTG |  | -- | exwtg1 | -- | X | -- | X | -- | X | 2nd Generation Renewable Models should replace these; potential numerical issues in base cases.
| GE Wind Turbine Control Model - Doubly Fed Induction Generator (DFIG) and Full Converter (FC) Models |  | -- | wndtge | -- | X | -- | X | -- | X | 2nd Generation Renewable Models should replace these; potential numerical issues in base cases.
| GE Wind Turbine Generator/Converter - DFAG and FC Models |  | -- | gewtg | -- | X | -- | X | -- | X | 2nd Generation Renewable Models should replace these; potential numerical issues in base cases.
| GE Wind Turbine Excitation (converter) Control Model for DFAG Generators |  | -- | exwtge | -- | X | -- | X | -- | X | 2nd Generation Renewable Models should replace these; potential numerical issues in base cases.
| GE Wind Turbine Plant-Level Supervisory Voltage/VAR Control |  | -- | wndvar | -- | -- | -- | -- | -- | -- | 2nd Generation Renewable Models should replace these; potential numerical issues in base cases.
| Solar Photovoltaic Generator/Converter Model |  | PVGU1 | pv1g | -- | X | -- | X | -- | --
| Solar Photovoltaic Electrical Control Model |  | PVEU1 | pv1e | -- | X | -- | X | -- | --
| Distributed photovoltaic system |  | -- | pvd1 | -- | X | -- | -- | -- | --
| Distributed Energy Resource Generator/Converter Model |  | DERAU1/DERA1 | der_a | X | X | X | X | -- | -- |  | https://www.wecc.org/Reliability/DER_A_Final_061919.pdf
Excitation System Models | IEEE Std 421.5 Type AC1A |  | ESAC1A | esac1a | X | X | X | X | X | X
| IEEE Std 421.5 Type AC1C |  | AC1C | esac1c | X | -- | -- | -- | -- | --
| Modified IEEE Std 421.5 Type AC1A |  | ESURRY | -- | -- | -- | X | -- | X | --
| IEEE Std 421.5 Type AC2A |  | ESAC2A | esac2a | X | X | X | X | X | X
| IEEE Std 421.5 Type AC2C |  | AC2C | esac2c | X | -- | -- | -- | -- | --
| IEEE Std 421.5 Type AC3A |  | ESAC3A | esac3a | X | X | X | X | X | X
| IEEE Std 421.5 Type AC3C |  | AC3C | esac3c | X | -- | -- | -- | -- | --
| IEEE Std 421.5 Type AC4A |  | ESAC4A | esac4a | X | X | X | X | X | X
| IEEE Std 421.5 Type AC4C |  | AC4C | esac4c | X | -- | -- | -- | -- | --
| IEEE Std 421.5 Type AC5A |  | ESAC5A | esac5a | X | X | X | X | X | X
| IEEE Std 421.5 Type AC5C |  | AC5C | esac5c | X | -- | -- | -- | -- | --
| IEEE Std 421.5 Type AC6A |  | ESAC6A | esac6a | [6 empty] | Issue in implementation of the VAMAX and VAMIN limits. Implementation does not match IEEE Standard. | https://siemens.force.com/SEMC2/s/article/PSS-E-User-Support
| IEEE Std 421.5 Type AC6A |  | AC6A | esac6a | X | X | X | X | X | X
| IEEE Std 421.5 Type AC6C |  | AC6C | esac6c | X | -- | -- | -- | -- | --
| Modified IEEE Std 421.5 Type AC6A (added speed multiplier) |  | AC6A | esac6a | -- | X | -- | -- | -- | -- | PSLF esac6a should be used instead of exac6a, since PSLF esac6a has the speed flag and is a standard IEEE model.
| IEEE Std 421.5 Type AC7B* |  | AC7B | esac7b | X | X | X | X | X | X
| IEEE AC7B Excitation System Model w/ OEL for Brushless Exciters and GE EX2100 Controls |  | AC7B | ex21br | -- | -- | -- | -- | -- | --
| IEEE Std 421.5 Type AC7C |  | AC7CU1/AC7C | esac7c | X | -- | -- | -- | -- | --
| IEEE Std 421.5 Type AC8B |  | AC8B | esac8b | X | X | X | X | X | X
| Modified IEEE Std 421.5 Type AC8B |  | ESAC8B | exac8b | X | X | X | X | X | X
| IEEE Std 421.5 Type AC8C |  | AC8CU1/AC8C | esac8c | X | -- | -- | -- | -- | --
| IEEE Std 421.5 Type AC9C |  | AC9CU1/AC9C | esac9c | X | -- | -- | -- | -- | --
| IEEE Std 421.5 Type AC10C |  | AC10CU1/AC10C | esac10c | X | -- | -- | -- | -- | --
| IEEE Std 421.5 Type AC11C |  | AC11CU1/AC11C | -- | X | -- | -- | -- | -- | --
| IEEE Std 421.5 Type DC1A |  | ESDC1A | esdc1a | X | X | X | X | X | X
| IEEE Std 421.5 Type DC1C |  | DC1C | esdc1c | X | -- | -- | -- | -- | --
| IEEE Std 421.5 Type DC2A |  | ESDC2A | esdc2a | X | X | X | X | X | X
| IEEE Std 421.5 Type DC2C |  | DC2C | esdc2c | X | -- | -- | -- | -- | --
| IEEE Std 421.5 Type DC3A |  | DC3A | esdc3a | X | X | X | X | X | X
| IEEE Std 421.5 Type DC4B |  | DC4B | esdc4b | X | X | X | X | X | X
| IEEE Std 421.5 Type DC4C |  | DC4CU1/DC4C | esdc4c | X | -- | -- | -- | -- | --
| IEEE Std 421.5 Type ST1A |  | ESST1A | esst1a | X | X | X | X | X | X
| IEEE Std 421.5 Type ST1C |  | ST1C | esst1c | X | -- | -- | -- | -- | --
| IEEE Std 421.5 Type ST2A |  | ESST2A | esst2a | X | X | X | X | X | X
| IEEE Std 421.5 Type ST2C |  | ST2C | esst2c | X | -- | -- | -- | -- | --
| IEEE Std 421.5 Type ST3A |  | ESST3A | esst3a | X | X | X | X | X | X
| IEEE Std 421.5 Type ST3C |  | ST3C | esst3c | X | -- | -- | -- | -- | --
| IEEE Std 421.5 Type ST4B |  | ESST4B | esst4b | X | X | X | X | X | X
| Modified IEEE Std 421.5 Type ST4B (without OEL & UEL inputs and Vgmax) |  | ESST4B | exst4b | -- | X | -- | X | -- | X
| IEEE Std 421.5 Type ST4C |  | ST4CU1/ST4C | esst4c | X | -- | -- | -- | -- | --
| IEEE Std 421.5 Type ST5B** |  | ST5B | esst5b | X | X | X | X | X | X
| IEEE Proposed Type ST5B Excitation System |  | URST5T | -- | X | -- | X | -- | X | --
| IEEE Std 421.5 Type ST5C |  | ST5C | esst5c | X | -- | -- | -- | -- | --
| IEEE Std 421.5 Type ST6B |  | ST6B | esst6b | X | X | X | X | X | X
| IEEE Std 421.5 Type ST6C |  | ST6CU1/ST6C | esst6c | X | -- | -- | -- | -- | --
| IEEE Std 421.5 Type ST7B |  | ST7B | esst7b | X | X | X | X | X | X
| IEEE Std 421.5 Type ST7C |  | ST7C | esst7c | X | -- | -- | -- | -- | --
| IEEE Std 421.5 Type ST8C |  | ST8CU1/ST8C | esst8c | X | -- | -- | -- | -- | --
| IEEE Std 421.5 Type ST9C |  | ST9CU1/ST9C | esst9c | X | -- | -- | -- | -- | --
| IEEE Std 421.5 Type ST10C |  | ST10CU1/ST1OC | esst10c | X | -- | -- | -- | -- | --
| 1968 IEEE Type 1+B127 |  | IEEET1 | ieeet1 | X | X | X | X | X | X
| Modified 1968 IEEE Type 1 |  | IEET1A | -- | X | -- | X | -- | X | --
| Modified 1968 IEEE Type 1 |  | IEET1B | -- | X | -- | X | -- | X | --
| 1968 IEEE Type 2 |  | IEEET2 | -- | X | -- | X | -- | X | --
| 1968 IEEE Type 3 |  | IEEET3 | -- | X | -- | X | -- | X | --
| 1968 IEEE Type 4 |  | IEEET4 | exdc4 | X | X | X | X | X | --
| Modified 1968 IEEE Type 4 |  | IEEET5 | -- | X | -- | X | -- | X | --
| Modified 1968 IEEE Type 4 |  | IEET5A | -- | X | -- | X | -- | X | --
| 1981 IEEE Type AC1 |  | EXAC1 | exac1 | X | X | X | X | X | X
| Modified 1981 IEEE Type AC1 (modified rate feedback source and with added speed multiplier) |  | EXAC1A | exac1a | X | X | X | X | X | X
| Modified 1981 IEEE Type AC1 |  | EXAC1A | exac1m | -- | -- | -- | -- | -- | --
| 1981 IEEE Type AC2 |  | EXAC2 | exac2 | X | X | X | X | X | X
| 1981 IEEE Type AC3 |  | EXAC3 | exac3 | X | X | X | X | X | --
| Modified 1981 IEEE Type AC3 |  | ESAC3A | exac3a | -- | X | -- | X | -- | X
| 1981 IEEE Type AC4 |  | EXAC4 | exac4 | X | X | X | X | X | X
| 1981 IEEE Type DC1 |  | IEEEX1 | exdc1 | X | X | X | X | X | X
| Modified 1981 IEEE Type DC1 |  | IEEEX2 | -- | X | -- | X | -- | X | --
| Modified 1981 IEEE Type DC1 |  | IEEX2A | -- | X | -- | X | -- | X | --
| 1981 IEEE Type DC2 |  | EXDC2 | exdc2a | X | X | X | X | X | X
| Modified 1981 IEEE Type DC2 |  | IEEEX2 | exdc2 | -- | X | -- | X | -- | X
| 1981 IEEE Type DC3 |  | IEEEX4 | exdc4 | X | X | X | X | X | X
| 1981 IEEE Type ST1 |  | EXST1 | exst1 | X | X | X | X | X | X
| 1981 IEEE Type ST2 |  | EXST2 | exst2 | X | X | X | X | X | X
| Modified 1981 IEEE Type ST2 |  | EXST2A | exst2a | X | X | X | X | X | X
| Modified 1981 IEEE Type ST2 |  | IEEEX3 | -- | X | -- | X | -- | X | --
| 1981 IEEE Type ST3 |  | EXST3 | exst3 | X | X | X | X | X | X
| Modified 1981 IEEE Type ST3 |  | ESST3A | exst3a | -- | X | -- | X | -- | X
| General Purpose Rotating Excitation System Model |  | REXSYS | rexs | X | X | X | X | X | X
| General Purpose Rotating Excitation System Model |  | REXSY1 | -- | X | -- | X | -- | X | --
| Proportional/Integral Excitation System Model |  | EXPIC1 | expic1 | X | X | X | X | X | X
| Manual Excitation Control with Field Circuit Resistance |  | -- | mexs | -- | X | -- | -- | -- | X
| General Purpose Transformer Fed Excitation System | ü | -- | texs | -- | X | -- | X | -- | X | Simplified, early generation model considered obsolete; other models more suitable. | SME input, IEEE Std. 421.5
| Bus or Solid Fed SCR Bridge Excitation System Model |  | SCRX | scrx | X | X | X | X | X | X
| Bus or Solid Fed SCR Bridge Excitation System Model Type NEBB (NVE) |  | EXNEBB | -- | -- | -- | -- | -- | -- | --
| Bus or Solid Fed SCR Bridge Excitation System Model Type NI (NVE) |  | EXNI | -- | -- | -- | -- | -- | -- | --
| Simplified Excitation System | ü | SEXS | sexs | X | X | X | X | X | X | Simplified, early generation model considered obsolete; other models more suitable. | SME input, IEEE Std. 421.5
| IVO Excitation System Model |  | IVOEX | exivo | X | X | X | -- | X | X
| ELIN Excitation System |  | CELIN | -- | -- | -- | X | -- | X | --
| Basler Static Voltage Regulator Feeding DC or AC Rotating Exciter |  | EXBAS | -- | X | -- | X | -- | X | --
| Brown-Boveri Transformer-Fed Static Excitation System Model |  | BBSEX1 | exbbc | X | X | X | X | X | X
| Static PI Transformer Fed Excitation System |  | EXELI | exeli | X | X | X | X | X | X
| VATECH (ELIN) Static Excitation System with PSS |  | -- | exeli2 | -- | -- | X | -- | X | --
| GE EX2000 Excitation System | ü | EX2000 | -- | X | -- | X | -- | X | -- | Field current limiter latch issue. Replace with AC7B in PSSE and ex21br in PSLF. | NERC EX2000 Modeling Notification
| AEP Rockport excitation system |  | EMAC1T | emac1t | X | -- | X | -- | X | --
| Czech Proportional/Integral Excitation System Model |  | BUDCZT | -- | -- | -- | -- | -- | -- | --
| High Dam Excitation System Model |  | URHIDT | -- | -- | -- | -- | -- | -- | --
Power System Stabilizer | Transient Excitation Boosting Stabilizer Model |  | BEPSST | -- | -- | -- | -- | -- | -- | --
| Dual-Input Signal Power System Stabilizer Model |  | IEE2ST | -- | X | -- | X | -- | X | --
| 1981 IEEE Power System Stabilizer |  | IEEEST | ieeest | X | X | X | X | X | X
| IVO Stabilizer Model |  | IVOST | -- | X | -- | -- | -- | -- | --
| Ontario Hydro Delta-Omega Power System Stabilizer |  | OSTB2T | -- | -- | -- | X | -- | -- | --
| Ontario Hydro Delta-Omega Power System Stabilizer |  | OSTB5T | -- | -- | -- | X | -- | -- | --
| IEEE Std 421.5-2005 Single-Input Stabilizer Model |  | PSS1A | pss1a | X | X | -- | X | -- | X
| 1992 IEEE Type Dual-Input Signal Stabilizer Model |  | PSS2A | pss2a | X | X | X | X | X | X
| IEEE Std 421.5-2005 PSS2B Dual-Input Stabilizer Model |  | PSS2B | pss2b | X | X | X | X | X | X
| IEEE Std 421.5-2016 PSS2C Dual-Input Stabilizer Model |  | PSS2CU1/PSS2C | pss2c | X | -- | -- | -- | -- | --
| IEEE Std 421.5-2005 PSS3B Dual-Input Stabilizer Model |  | PSS3B | pss3b | -- | X | -- | X | X | X
| IEEE Std 421.5-2016 PSS3C Dual-Input Stabilizer Model |  | PSS3C | pss3c | X | -- | -- | -- | -- | --
| IEEE Std 421.5-2005 PSS4B Dual-Input Stabilizer Model |  | PSS4B | -- | -- | -- | -- | -- | -- | --
| IEEE Std 421.5-2016 PSS4C Dual-Input Stabilizer Model |  | PSS4C | pss4c | X | -- | -- | -- | -- | --
| IEEE Std 421.5-2016 PSS5C Dual-Input Stabilizer Model |  | PSS5C | pss5c | X | -- | -- | -- | -- | --
| IEEE Std 421.5-2016 PSS6C Dual-Input Stabilizer Model |  | PSS6CU1/PSS6C | pss6c | X | -- | -- | -- | -- | --
| IEEE Std 421.5-2016 PSS7C Dual-Input Stabilizer Model |  | PSS7CU1/PSS7C | pss7c | X | -- | -- | -- | -- | --
| PTI Microprocess-Based Stabilizer Model |  | PTIST1 | -- | -- | -- | X | -- | X | --
| PTI Microprocess-Based Stabilizer Model |  | PTIST3 | -- | -- | -- | X | -- | X | --
| Speed Sensitive Stabilizer Model |  | STAB1 | -- | X | -- | X | -- | X | --
| ASEA Power Sensitive Stabilizer Model |  | STAB2A | -- | X | -- | X | X | X | --
| Power Sensitive Stabilizer Model |  | STAB3 | -- | X | -- | X | -- | X | --
| Power Sensitive Stabilizer Model |  | STAB4 | -- | X | -- | X | -- | X | --
| Dual-Input Signal Power System Stabilizer Model |  | ST2CUT | wsccst | X | X | X | X | X | X
| Dual Input Stabilizer (IEEE Type PSS2A) + Voltage Boost Signal Transient Stabilizer and Vcutoff |  | -- | psssb | -- | X | -- | X | -- | X
| WECC Supplementary Signal for Static Var System |  | STBSVC | -- | X | -- | X | -- | X | --
| Synchronous Condenser Auxiliary Control Model |  | SYNAXBU1 | -- | -- | -- | -- | -- | -- | --
| Single Input PSS for SVSMO1, SVSMO2, and SVSMO3 |  | -- | psssvc | -- | -- | -- | -- | -- | --
Current Compensation Models | Cross-Current Compensation Model with Reactive Current Feedback |  | CCOMP4U1 | ccomp4 | -- | X | -- | -- | -- | --
| Voltage Regulator Compensating Model |  | COMP | ** | X | -- | X | -- | X | --
| Cross and Joint Current Compensation Model |  | COMPCC | ccomp | X | X | -- | -- | X | --
| IEEE Std 421.5 Current Compensator |  | IEEEVC | † | X | † | X | † | X | †
| Remote Bus Voltage Signal Model |  | REMCMP | ** | X | -- | X | -- | X | --
Turbine-Governor Models | Steam Plant Boiler Turbine-Governor Model |  | -- | ccbt1 | -- | X | -- | -- | -- | X | Similar but different than TGOV5.
| Combined Cycle Plant Steam Turbine Model |  | UCBGT | ccst3 | -- | -- | -- | -- | -- | X
| GE Frame 6, 7, and 9 Gas Turbine Model |  | -- | gegt1 | -- | -- | -- | -- | -- | -- | Detailed model. Encouraged to use generic model - GGOV1 - for interconnection-wide modeling.
| General Purpose (Gas Turbine & Single Shaft CC) Turbine-Governor Model |  | GGOV1 | ggov1 | X | X | X | X | X | X
| General Governor Model with Frequency-Dependent Fuel Flow Limit |  | -- | ggov2 | -- | X | -- | -- | -- | X
| General Governor Model with GE Gas Turbine Control Features |  | -- | ggov3 | -- | X | -- | X | -- | X
| LM 2500 Aero-Derivative Gas Turbine Governor Model | ü | -- | lm2500 | -- | -- | -- | -- | -- | -- | No supporting documentation (block diagrams), proprietary model. Use GGOV1.
| LM 6000 Aero-Derivative Gas Turbine Governor Model | ü | -- | lm6000 | -- | -- | -- | -- | -- | -- | No supporting documentation (block diagrams), proprietary model. Use GGOV1.
| Single Shaft Combined Cycle Plant Model |  | -- | stag1 | -- | -- | -- | -- | -- | --
| Woodward 2301 Governor and Basic Turbine Model |  | -- | w2301 | -- | X | -- | X | -- | X
| Brown-Boveri Turbine-Governor Model |  | BBGOV1 | -- | -- | -- | -- | -- | X | --
| Cross Compound Turbine-Governor Model |  | CRCMGV | crcmgv | X | X | X | X | X | X
| Woodward Diesel Governor Model |  | DEGOV | -- | X | -- | -- | -- | X | --
| Woodward Diesel Governor Model |  | DEGOV1 | degov1 | X | -- | X | -- | X | --
| WECC Gas Turbine Governor Model | ü | URGS3T | gast | X | X | X | X | X | X | Simplistic representation of steam turbine-governor system. Insufficient model capability of modern digital controls.
| Gas Turbine-Governor Model | ü | GAST | -- | X | -- | X | -- | X | -- | simple representations of a turbine-governor control system. Insufficient model capability and flexibility for most modern digital gas turbine-governor control systems. | Modeling Notification - Gas Turbine Governor Modeling
| Gas Turbine-Governor Model | ü | GAST2A | -- | X | -- | X | -- | X | -- | simple representations of a turbine-governor control system. Insufficient model capability and flexibility for most modern digital gas turbine-governor control systems. | Modeling Notification - Gas Turbine Governor Modeling
| Gas turbine-governor | ü | GASTWD | -- | X | -- | X | -- | X | -- | simple representations of a turbine-governor control system. Insufficient model capability and flexibility for most modern digital gas turbine-governor control systems. | Modeling Notification - Gas Turbine Governor Modeling
| Hydro Turbine-Governor Model |  | HYGOV | hygov | X | X | X | X | X | X
| Hydro Turbine-Governor Model |  | HYGOV2 | -- | X | -- | X | -- | X | -- | Superceded by hygov4 or any other updated hydro model.
| Hydro Turbine-Governor Lumped Parameter Model |  | HYGOVM | -- | -- | -- | -- | -- | -- | --
| Fourth Order Lead-Lag Hydro-Turbine Model |  | HYGOVR1 | hygovr | X | X | X | X | X | X
| Hydro Turbine-Governor Traveling Wave Model |  | HYGOVT | -- | -- | -- | -- | -- | -- | --
| Hydro Turbine-Governor Model |  |  | h6b | -- | -- | -- | X | -- | --
| Model to Manage Parameter Data for h6b Hydro Turbine-Governor Model |  | -- | h6bd | -- | X | -- | -- | -- | --
| Hydro Governor Model for up to 4 Units on Common Penstock |  | -- | hygov8 | -- | -- | -- | -- | -- | --
| Hydro Turbine-Governor (plants w/ straightforward penstock config + PID governor, blade angle for Kaplan) |  | -- | hypid | -- | X | -- | -- | -- | --
| Hydro Turbine w/ Woodward Electro-Hydraulic PID Governor, Penstock, Surge Tank, and Inlet Tunnel |  | -- | hyst1 | -- | -- | -- | -- | -- | --
| 1981 IEEE Type 1 General Steam Turbine-Governor Model |  | IEEEG1 | ieeeg1 | X | -- | X | -- | X | -- | Use the WSIEG1 model instead. PSS/E WSIEG1 = PSLF IEEEG1.
| 1981 IEEE Type 2 General Approx. Linear Ideal Hydro Model | ü | IEEEG2 | -- | X | -- | X | -- | X | -- | Model does not have an effective turbine model and an oversimplified governor model applicable only to first swing stability. Outdated. Typically recommend using a hygov model instead (no parameter-by-parameter replacement though.)
| 1981 IEEE Type 3 General Mechanical-Hydraulic Model |  | IEEEG3 | ieeeg3 | X | X | X | X | X | X
| Hydro Turbine-Governor (plants with straightforward penstock config + hydraulic govs of 'dashpot' type) |  | IEEEG3 | hygov4 | -- | X | -- | X | -- | X
| 1973 IEEE General Steam Non-Reheat |  | IEESGO | -- | X | -- | X | -- | X | -- | Should be converted to WSIEG1 (PSS/E) or IEEEG1 (PSLF); does not represent rate limits for control valve or intentional deadband.
| IVO Turbine-Governor Model |  | IVOGO | -- | -- | -- | -- | -- | X | --
| Hydro Turbine-Governor Model |  | PIDGOV | pidgov | X | X | X | X | X | X
| Pratt & Whitney Turboden Turbine-Governor Model |  | PWTBD1 | -- | -- | -- | -- | -- | -- | --
| Torsional-Elastic Shaft Model for 25 Masses |  | SHAF25 | -- | -- | -- | -- | -- | -- | --
| Steam Turbine-Governor Model |  | TGOV1 | tgov1 | X | X | X | X | X | X
| Steam Turbine-Governor Model w/ Fast Valving |  | TGOV2 | -- | X | -- | X | -- | X | -- | Detailed model used for special cases.
| 1973 Modified IEEE Type 1 General Steam Turbine-Governor Model w/ Fast Valving |  | TGOV3 | tgov3 | X | X | X | X | X | X | Detailed model used for special cases.
| Modified IEEE Type 1 General Steam Turbine-Governor Model w/ PLU and EVA |  | TGOV4 | -- | -- | -- | -- | -- | -- | -- | Detailed model used for special cases.
| Modified IEEE Type 1 General Steam Turbine-Governor Model w/ Boiler Controls |  | TGOV5 | -- | X | -- | -- | -- | X | -- | Detailed model that includes boiler controls; used for special studies.
| Czech Hydro or Steam Turbine-Governor Model |  | TURCZT | -- | -- | -- | -- | -- | -- | --
| Tail Water Depression Hydro Governor Model 1 |  | TWDM1T | -- | -- | -- | -- | -- | -- | --
| Tail Water Depression Hydro Governor Model 2 |  | TWDM2T | -- | -- | -- | -- | -- | -- | --
| Combined Cycle - Single Shaft Turbine-Governor Model |  | URCSCT | -- | -- | -- | -- | -- | -- | --
| Woodward Electronic Hydro Governor Model |  | WEHGOV | -- | X | -- | X | -- | X | --
| Westinghouse Digital Governor Model for Gas Turbines | ü | WESGOV | -- | X | -- | X | -- | X | -- | simple representations of a turbine-governor control system. Insufficient model capability and flexibility for most modern digital gas turbine-governor control systems. | Modeling Notification - Gas Turbine Governor Modeling
| Woodward PID Hydro Governor Model |  | WPIDHY | -- | X | -- | X | -- | X | --
| WECC Double Derivative Hydro Governor Model |  | WSHYDD | g2wscc | X | X | X | X | X | X
| WECC GP Hydro Turbine-Governor Model |  | WSHYGP | gpwscc | X | X | X | X | X | X | Use hyg3 or HYG3 model. | WECC Approved Dynamic Model Library
| Hydro Turbine with American Governor Company controller |  | H6E | h6e | -- | -- | X | X | -- | -- | This is the preferred model for American Governor Company controlled hydro facilities
| PID Governor, Double-Derivative Governor, and Turbine (WECC GP governor, WECC G2 turbine-governor) |  | HYG3 | hyg3 | -- | X | -- | X | -- | X
| Modified IEEE Type 1 General Steam Turbine-Governor Model w/ Speed Deadband |  | WSIEG1 | ieeeg1 | X | X | X | X | X | --
Load Controller Models | Turbine Load Controller Model |  | LCFB1 | lcfb1 | X | X | X | X | X | X
Load Models | Induction Generator Model with Rotor Flux Transients |  | CIMTR1 | -- | X | -- | X | -- | X | --
| Induction Motor Model with Rotor Flux Transients |  | CIMTR2 | -- | X | -- | X | -- | X | --
| Induction Generator Model with Rotor Flux Transients |  | CIMTR3 | genind | X | -- | X | -- | X | --
| Induction Motor Model with Rotor Flux Transients |  | CIMTR4 | motor1 | X | X | X | X | X | X
| Induction Motor Model |  | CIM5BL | -- | -- | -- | -- | -- | -- | --
| Induction Motor Model |  | CIM6BL | -- | -- | -- | -- | -- | -- | --
| Induction Motor Model |  | CIMWBL | motorw | -- | X | X | X | X | X
| IEEE Load Model |  | IEEL__ | _lwscc | X | -- | X | X | X | --
| Load Frequency Model |  | LDFR__ | -- | X | -- | X | -- | X | --
| Extended-Term Load Reset Model |  | EXTLBL | -- | -- | -- | -- | -- | -- | --
| Complex Load Model |  | CLOD__ | clod | X | -- | X | -- | X | --
| Composite Load Model |  | CMLDBLU2 | cmpldw | -- | X | X | X | X | X
| Composite Load Model w/ DER Component |  | CMLDBLDGU2 | cmpldwg | -- | -- | -- | -- | -- | --
| Composite Load Model w/ Modular Capability |  | -- | cmpldw2 | -- | X | -- | -- | -- | --
| Performance-Based Model of Single Phase Air Conditioner Motor Model |  | ACMTBLU1 | ld1pac | -- | X | -- | -- | -- | --
| Phasor Model of Single-Phase Air-Conditioner Compressor Motor | ü |  | motorc | -- | X | -- | -- | -- | -- | Experimental model. | PSLF Manual
Static Var Systems and FACTS | WECC Generic Continuous Control SVC Model |  | SVSMO1T2 | svsmo1 | -- | X | X | X | -- | X
| WECC Generic Discrete Control SVC Model |  | SVSMO2T2 | svsmo2 | -- | X | X | X | -- | X
| WECC Generic STATCOM-Based SVC Model |  | SVSMO3T2 | svsmo3 | -- | X | X | X | -- | X
| SCR Controlled Static VAR Source Model |  | CSVGN1 | -- | X | -- | X | -- | X | --
| SCR Controlled Static VAR Source Model |  | CSVGN3 | -- | X | -- | X | -- | X | --
| SCR Controlled Static VAR Source Model |  | CSVGN4 | -- | X | -- | X | -- | X | --
| WECC Controlled Static VAR Source Model |  | CSVGN5 | vwscc | X | X | X | X | X | X
| WECC Controlled Static VAR Source Model |  | CSVGN6 | -- | X | -- | X | -- | -- | --
| Switched Shunt Model |  | SWSHNT | msc1 | X | X | X | -- | -- | --
| American Superconductor DSMES Device |  | CDSMS1 | -- | -- | -- | -- | -- | -- | --
| Static Condenser FACTS Model |  | CSTATT | -- | X | -- | X | -- | X | --
| Static Condenser (modeled as FACTS in power flow) |  | CSTCNT | -- | -- | -- | X | -- | -- | --
| ABB SVC Model |  | ABBSVC1 | -- | -- | -- | X | -- | -- | --
| SVC for Switched Shunt |  | CHSVCT | -- | -- | -- | X | -- | X | --
| SVC for Switched Shunt |  | CSSCST | -- | X | -- | X | -- | X | --
| EPRI Superconducting Electromagnetic Energy Storage FACTS Model |  | CSMEST | -- | -- | -- | -- | -- | -- | --
| EPRI Battery Energy Storage FACTS Model |  | CBEST | -- | X | -- | -- | -- | X | --
Protection and Other Models | Generic Generator Protection System |  | -- | gp1, gp2, gp3 | -- | X | -- | X | -- | X
| Under-/Over-Frequency Generator Bus Disconnection Relay |  | FRQTPAT | lhfrt | X | X | X | X | -- | X
| Under-/Over-Frequency Generator Trip Relay |  | FRQDCAT | -- | X | -- | X | -- | -- | --
| Under-/Over-Voltage Generator Bus Disconnection Relay |  | VTGTPAT | lhvrt | X | X | X | X | X | X
| Under-/Over-Voltage Generator Trip Relay |  | VTGDCAT | -- | X | -- | X | -- | X | --
| Time-Inverse Overcurrent Relay |  | TIOCR1 | locti | X | X | x | -- | X | X
| Definite Time Underfrequency Load Shedding Relay |  | LDS3BL | lsdt1, lsdt9, lsdt7, lsdt8 | X | X | X | X | -- | X
| Definite Time Undervoltage Load Shedding Relay |  | LDS3BL | lsdt2, lsdt3, lsdt3a | -- | X | X | X | -- | X
| Definite Time Undervoltage Load Shedding Relay |  | LDS3BL | lsdt2, lsdt3, lsdt3a | -- | X | X | X | -- | X
| Out-of-Step Relay with 3 Zones (Lens, Tomato, or Circle) |  | CIROS1 | ooslen | -- | X | -- | -- | -- | X
| Out-of-Step Relay with 3 Zones (Lens, Tomato, Circle, or Rectangle) |  | CIROS1 | ooslnq | -- | X | -- | -- | -- | --
| Out-of-Step Mho Relay with Blinders |  | SLNOS1 | oosmho | -- | X | -- | -- | -- | --
| Metal Oxide Varistor and Bypass Protection for Series Capacitor |  | -- | scmov | -- | X | -- | -- | -- | --
| Switched Capacitor Bank Model |  | SWCAPT | -- | -- | -- | -- | -- | -- | --
| Mechanically Switched Capacitor |  | -- | msc1 | -- | X | -- | -- | -- | --
| Mechanically Switched Reactor |  | -- | msr1 | -- | X | -- | -- | -- | --
| Mechanically Switched Line Reactor |  | -- | mslr1 | -- | X | -- | -- | -- | --
| Mechanically Switched Shunt |  | -- | mss1 | -- | -- | -- | -- | -- | --
| Mechanically Switched Shunt |  | -- | mss2 | -- | -- | -- | -- | -- | --
| Over-Excitation Limiter for Synchronous Machine Excitation System |  | -- | oel1 | -- | X | -- | X | -- | X
| IEEE Std 421.5-2016 OEL1B Overexcitation Limiter |  | OEL1B | -- | X | -- | -- | -- | -- | --
| IEEE Std 421.5-2016 OEL2C Overexcitation Limiter | GAST: OEL2CU1/OEL2C; --: oel2c
| IEEE Std 421.5-2016 OEL3C Overexcitation Limiter |  | OEL3C | oel3c | X | -- | -- | -- | -- | --
| IEEE Std 421.5-2016 OEL4C Overexcitation Limiter |  | OEL4C | oel4c | X | -- | -- | -- | -- | --
| IEEE Std 421.5-2016 OEL5C Overexcitation Limiter |  | OEL5C | oel5c | X | -- | -- | -- | -- | --
| IEEE Std 421.5-2016 UEL1 Underexcitation Limiter |  | UEL1 | uel1 | X | -- | -- | -- | -- | --
| IEEE Std 421.5-2016 UEL2 Underexcitation Limiter |  | UEL2 | -- | X | -- | -- | -- | -- | --
| IEEE Std 421.5-2016 UEL2C Underexcitation Limiter |  | UEL2CU1/UEL2C | uel2c | X | -- | -- | -- | -- | --
IEEE Std 421.5-2016 SCL1C Stator Current Limiter | bar: -- to --
IEEE Std 421.5-2016 SCL2C Stator Current Limiter | bar: -- to --
IEEE Std 421.5-2016 DEC1A Discontinuous Excitation Control | bar: GAST to --
IEEE Std 421.5-2016 DEC2A Discontinuous Excitation Control | bar: GAST to --
IEEE Std 421.5-2016 DEC3A Discontinuous Excitation Control | bar: GAST to --
| Load Tap Changer Model |  | OLTC1T | ltc1 | -- | X | -- | -- | -- | --
| Variable Frequency Transformer or Rotary Phase Shift Regulator |  | VFT1 | vft | -- | X | -- | -- | -- | --
† - Current compensator is part of the generator model
** - Built into generator model in PSLF
* PSSE: Area-based: __=AR; Bus-based: __=BL; Zone-based: __=ZN; All: __=AL
* PSLF: Area-based: __=a; Bus-based: __=b; Zone-based: __=z; All: __=w
^ For Siemens PTI PSS®E implementation, the "DU" version of the model is also acceptable.
Applicable Reference Materials and Additional Reading:
[1] "IEEE Guide for Synchronous Generator Modeling Practices and Applications in Power System Stability Analyses," IEEE Std 1110-2002.
[2] Undrill, J., "The gentpj model," November 19, 2007 (updated June 19, 2012). http://www.wecc.biz/
[3] "IEEE Recommended Practice for Excitation System Models for Power System Stability Studies," IEEE Std 421.5-2005.
[4] “Computer Representation of Excitation Systems," IEEE Transactions on Power Apparatus and Systems, Vol. PAS-87, No. 6, pp. 1460-1468, 1968 (Committee Report).
[5] "Excitation System Models for Power System Stability Studies," IEEE Transactions on Power Apparatus and Systems, Vol. PAS-100, No. 2, pp. 494-509, 1981 (Committee Report).
[6] IEEE Task Force on Overall Plant Response, “Dynamic Models for Steam and Hydro Turbines in Power System Studies”, IEEE Trans. on PAS, Vol PAS-92, Nov-Dec 1973, pp. 1904-1915.
[7] Task Force on Turbine-Governor Modeling, "Dynamic Models for Turbine-Governors in Power System Studies," IEEE Technical Report, PES-TR1, Jan. 2013.
[8] WECC M&VWG, "Composite Load Model for Dynamic Simulations" Ver 1.0, June 12, 2012.
[9] WECC M&VWG, "WECC Wind Power Plant Dynamic Modeling Guide," November 2010.
[10] EPRI, "Specification of the Second Generation Generic Models for Wind Turbine Generators," September 20, 2013. and WECC M&VWG, "Generic Solar Photovoltaic System Dynamic Simulation Model Specification," September 2012.
[11] WECC, "Generic Static Var System Models for the Western Electricity Coordinating Council" April 18, 2011.
[12] W. I. Rowen, “Simplified Mathematical Representations of Heavy Duty Gas Turbines”, ASME Paper 83‐GT‐63 and ASME Journal of Engineering for Power, October 1983, pages 865‐869. [GAST2A reference]
[13] Periera, L. et al, "A New Thermal Governing Approach in the WECC," IEEE Transaction on Power System, Vol. 18, No. 2, pp. 819-829, May 2003.
[14] WECC M&VWG, "Cross-current Compensation Model Specification," August 2015.
[15] EPRI, "Simple Model Specification for Battery Energy Storage System," March 6, 2015.
[W1] WECC Approved Dynamic Model Library. http://www.wecc.biz/
[W2] WECC M&VWG, "WECC Wind Power Plant Dynamic Modeling Guide," April 2014.
[W3] WECC M&VWG, "WECC PV Power Plant Dynamic Modeling Guide," April 2014.
[E1] EPRI, "Proposed Changes to the WECC WT3 Generic Model for Type 3 Wind Turbine Generators," September 27, 2013.
[E2] EPRI, "Proposed Changes to the WECC WT4 Generic Model for Type 4 Wind Turbine Generators," January 23, 2013.
[16] Q. Wang, “GENQEC Generator Dynamic Model”, July, 2019. https://www.wecc.org/Administrative/GENQEC%20Model%20Specification.pdf
[17] Q.Y. Wang, S. Wang, “A New High Accuracy Generator Dynamic Model”, 2018 IEEE PES Asia-Pacific Power and Energy Engineering Conference (APPEEC).
Note on D16: Author: GENTPJU1 (v.33), GENTPJ (v.34)
Note on H23: Author: Defined in a separate dynamic data file (*.dat)
Note on I23: Author: Defined in a separate dynamic data file (*.dat)
Note on H24: Author: Defined in a separate dynamic data file (*.dat)
Note on I24: Author: Defined in a separate dynamic data file (*.dat)
Note on D43: Author: WTDTAU1 (v. 33) / WTDTA1 (v. 34)
Note on D46: Author: WTPTAU1 (v. 33) / WTPTA1 (v. 34)
Note on D50: Author: WTARAU1 (v.33) / WTARA1 (v.34)
Note on D51: Author: WTTQAU1 (v. 33) / WTTQA1 (v. 34)
Note on D56: Author: REGCAU1 (v. 33) / REGCA1 (v. 34)
Note on D58: Author: REECAU1 (v. 33) / REECA1 (v. 34)
Note on D59: Author: REPCTAU1 (v. 33) / REPCTA1 (v. 34) for Type 3;
Note on D61: Author: REECBU1 (v. 33) / REECB1 (v. 34)
Note on D65: Author: REAX4BU1 for Type 4; REAX3BU1 for Type 3
Note on D69: Author: Manufacturer specific model
Note on D70: Author: Manufacturer specific model
Note on D71: Author: Manufacturer specific model
Note on D72: Author: Manufacturer specific model
Note on D73: Author: Manufacturer specific model
Note on D91: Author: in version 34. Until then, use the USAC6AU model.
Note on D93: Author: ESAC6A (v. 33 & v.34); USAC6AU (v. 33) AC6A (v. 34)
Note on D209: Author: Model from PTI
Note on D279: Author: SVSMO1U2 (v. 33) / SVSMO1T2 (v. 34)
Note on D280: Author: SVSMO2U2 (v. 33) / SVSMO2T2 (v. 34)
Note on D281: Author: SVSMO3U2 (v. 33) / SVSMO3T2 (v. 34)

## Version Tracking
NERC LIST OF ACCEPTABLE MODELS FOR INTERCONNECTION-WIDE MODELING
Last Updated: February 2021
| Version | Date | Description | Approval Date
| 1 | 2017-04-01 | Initial list posted. | 2017-01-19
| 2 | 2017-04-25 | Disallowed LM2500, LM6000 based on no documentation and discussions with GE. Reformatted list. Added IEEE Std. 421.5-2016 new models to the list (not yet implemented in most software platforms).
| 3 | 2017-04-27 | Added gegt1 to the list of not recommended models. Detailed model best used for detailed studies or islanding studies, but not for interconnection-wide modeling. GGOV1 more suitable for these studies. Change made based on SME input.
| 4 | 2017-05-09 | Added blue color code to identify models that are industry accepted yet not yet implemented by software vendors.
| 5 | 2017-05-12 | Added GENTPJ Modeling Notification to comments and reference for GENROU, GENROE, GENSAL, GENSAE. Rearranged models for readability.
| 6 | 2017-06-07 | Changed CGEN1, GENSAE, TGOV2, TGOV3, TGOV4 to 'not recommended' from 'disallowed' based on PPMVTF input. Added comments on multiple models. Removed FRECHG model from 'not recommended'. Specialized model, but suitable under rare situations. Removed wt2e model from 'disallowed'. Disallowed SEX and TEXS based on subject matter expert input and simplistic representation of excitation system controls.
| 7 | 2017-08-10 | Disallowed GAST, GAST2A, GASTWD, and WESGOV. Added link to Modeling Notification. NERC SAMS approved updated list. | 2017-08-10
| 8 | 2017-08-21 | New version posted to NERC SAMS webpage.
| 9 | 2018-09-21 | Added description of why IEEEG2 is not recommended. Added hygov2 to the list of not recommended models. | 2018-11-07
| 10 | 2018-11-07 | Added reecb to the list of not recommended models, if momentary cessation is used by the resource. | 2018-11-07
| 11 | 2018-11-09 | New version posted to NERC SAMS webpage.
| 12 | 2019-07-30 | Updated ESAC6A and AC6A models for PSLF and PSS/E versions. Added statement about the DU models in PSS®E implementation being acceptable. Added REAX3BU1, SVCAXBU1, FCTAXBU1, and SYNAXBU1 models. Update to disclaimer language to clarify use of models not on list and to encourage use of generic models where possible. Added DER_A model. | 2019-08-01
| 13 | 2019-10-31 | REEC_B model changed to lit of unacceptable models per IRTPF input and Subject Matter Experts Added Clarifying language over "Future use of unacceptable models" - Changed to "Future model submittals or renewals using this model should be prohibited" Added PTI Siemens models for REECC, …... Took off versioning of PSLF, PSS/E and other tools | 2019-10-31
| 14 | 2020-01-10 | Added h6e and H6E/H6EU1 to list of models with note of preference on usage for American Governor Company models. Additionally, the IEEE Std. 421.5(2016) models were changed from blue to white to indicate availability in the softwares listed.
| 15 | 2020-07-08 | Added idication for the following models made available in PSS/E: AC1C (AC1C in rev. 34.6), AC2C (AC2C in rev. 34.6), AC3C (AC3C in rev. 34.6), AC4C, AC5C, AC6C, AC7C, AC8C, AC9C, AC11C, DC1C, DC2C, DC4C, ST1C, ST4C, ST5C, ST6C, ST7C, ST8C, ST9C, ST10C, PSS2C (PSS2CU1 in rev. 34.6), PSS6C, PSS7C, OEL2C (OEL2CU1 in rev. 34.6), UEL2C (UEL2CU1 in rev. 34.6). Added Powerworld indication of similar models.
| 16 | 2021-02-16 | Updated Purpose and Background tab.
| 17 | 2021-06-08 | Updated Model names with latest available implemented models. Added genqec, regc_b, reec_d, wtgp_b, and wtgt_b models.
18
19
20
21
22
23
24
25